## parameters
| version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.10.1 | FALSE | FALSE | dickert_lv_network withshort-range feeders, cableand multiplecustomers in averagecase | 50 | 1

## bus
| name | vn_kv | type | zone | in_service
0 | busbar | 0.4 | b |  | TRUE
1 | bus 1 | 0.4 | m | Feeder B0 | TRUE
2 | bus 2 | 0.4 | m | Feeder B0 | TRUE
3 | bus 3 | 0.4 | m | Feeder B0 | TRUE
4 | bus 4 | 0.4 | m | Feeder B0 | TRUE
5 | bus 5 | 0.4 | m | Feeder B0 | TRUE
6 | bus 6 | 0.4 | m | Feeder B0 | TRUE
7 | bus 7 | 0.4 | m | Feeder B1 | TRUE
8 | bus 8 | 0.4 | m | Feeder B1 | TRUE
9 | bus 9 | 0.4 | m | Feeder B1 | TRUE
10 | bus 10 | 0.4 | m | Feeder B1 | TRUE
11 | bus 11 | 0.4 | m | Feeder B1 | TRUE
12 | bus 12 | 0.4 | m | Feeder B1 | TRUE

## load
index | name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 |  | 1 | 0.0044405 | 0.0014595 | 0 | 0 | 0.01 | 1 | TRUE | wye
1 |  | 2 | 0.0044405 | 0.0014595 | 0 | 0 | 0.01 | 1 | TRUE | wye
2 |  | 3 | 0.0044405 | 0.0014595 | 0 | 0 | 0.01 | 1 | TRUE | wye
3 |  | 4 | 0.0044405 | 0.0014595 | 0 | 0 | 0.01 | 1 | TRUE | wye
4 |  | 5 | 0.0044405 | 0.0014595 | 0 | 0 | 0.01 | 1 | TRUE | wye
5 |  | 6 | 0.0044405 | 0.0014595 | 0 | 0 | 0.01 | 1 | TRUE | wye
6 |  | 7 | 0.0044405 | 0.0014595 | 0 | 0 | 0.01 | 1 | TRUE | wye
7 |  | 8 | 0.0044405 | 0.0014595 | 0 | 0 | 0.01 | 1 | TRUE | wye
8 |  | 9 | 0.0044405 | 0.0014595 | 0 | 0 | 0.01 | 1 | TRUE | wye
9 |  | 10 | 0.0044405 | 0.0014595 | 0 | 0 | 0.01 | 1 | TRUE | wye
10 |  | 11 | 0.0044405 | 0.0014595 | 0 | 0 | 0.01 | 1 | TRUE | wye
11 |  | 12 | 0.0044405 | 0.0014595 | 0 | 0 | 0.01 | 1 | TRUE | wye

## sgen
| name | bus | p_mw | q_mvar | sn_mva | scaling | in_service | type | current_source | controllable
0 | PV-bus 5 | 5 | 0 | 0 | 0.01 | 1 | TRUE | wye | TRUE | TRUE
1 | PV-bus 3 | 3 | 0 | 0 | 0.01 | 1 | TRUE | wye | TRUE | TRUE
2 | PV-bus 8 | 8 | 0 | 0 | 0.01 | 1 | TRUE | wye | TRUE | TRUE
3 | PV-bus 7 | 7 | 0 | 0 | 0.01 | 1 | TRUE | wye | TRUE | TRUE
4 | PV-bus 11 | 11 | 0 | 0 | 0.008 | 1 | TRUE | wye | TRUE | TRUE
5 | PV-bus 12 | 12 | 0 | 0 | 0.009 | 1 | TRUE | wye | TRUE | TRUE
6 | PV-bus 10 | 10 | 0 | 0 | 0.008 | 1 | TRUE | wye | TRUE | TRUE
7 | PV-bus 4 | 4 | 0 | 0 | 0.01 | 1 | TRUE | wye | TRUE | TRUE
8 | PV-bus 1 | 1 | 0 | 0 | 0.009 | 1 | TRUE | wye | TRUE | TRUE
9 | PV-bus 9 | 9 | 0 | 0 | 0.009 | 1 | TRUE | wye | TRUE | TRUE
10 | PV-bus 6 | 6 | 0 | 0 | 0.008 | 1 | TRUE | wye | TRUE | TRUE
11 | PV-bus 2 | 2 | 0 | 0 | 0.01 | 1 | TRUE | wye | TRUE | TRUE
12 | Slack Gen | 0 | 0 | 0 | 1 | 1 | TRUE | wye | TRUE | TRUE

## ext_grid
index | name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 0 | 1 | 0 | 1 | TRUE

## line
index | name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 |  | NAYY 4x150 SE | 0 | 1 | 0.05 | 0.208 | 0.08 | 0 | 0 | 1000 | 1 | 1 | cs | TRUE
1 |  | NAYY 4x150 SE | 1 | 2 | 0.05 | 0.208 | 0.08 | 0 | 0 | 1000 | 1 | 1 | cs | TRUE
2 |  | NAYY 4x150 SE | 2 | 3 | 0.05 | 0.208 | 0.08 | 0 | 0 | 1000 | 1 | 1 | cs | TRUE
3 |  | NAYY 4x150 SE | 3 | 4 | 0.05 | 0.208 | 0.08 | 0 | 0 | 1000 | 1 | 1 | cs | TRUE
4 |  | NAYY 4x150 SE | 4 | 5 | 0.05 | 0.208 | 0.08 | 0 | 0 | 1000 | 1 | 1 | cs | TRUE
5 |  | NAYY 4x150 SE | 5 | 6 | 0.05 | 0.208 | 0.08 | 0 | 0 | 1000 | 1 | 1 | cs | TRUE
6 |  | NAYY 4x150 SE | 0 | 7 | 0.05 | 0.208 | 0.08 | 0 | 0 | 1000 | 1 | 1 | cs | TRUE
7 |  | NAYY 4x150 SE | 7 | 8 | 0.05 | 0.208 | 0.08 | 0 | 0 | 1000 | 1 | 1 | cs | TRUE
8 |  | NAYY 4x150 SE | 8 | 9 | 0.05 | 0.208 | 0.08 | 0 | 0 | 1000 | 1 | 1 | cs | TRUE
9 |  | NAYY 4x150 SE | 9 | 10 | 0.05 | 0.208 | 0.08 | 0 | 0 | 1000 | 1 | 1 | cs | TRUE
10 |  | NAYY 4x150 SE | 8 | 11 | 0.05 | 0.208 | 0.08 | 0 | 0 | 1000 | 1 | 1 | cs | TRUE
11 |  | NAYY 4x150 SE | 11 | 12 | 0.05 | 0.208 | 0.08 | 0 | 0 | 1000 | 1 | 1 | cs | TRUE

## line_std_types
idx | Name | c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha
1 | NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403
2 | NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403
3 | NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403
4 | NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403
5 | NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403
6 | NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403
7 | NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403
8 | NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403
9 | NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403
10 | NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403
11 | NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403
12 | NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403
13 | NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403
14 | NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403
15 | NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403
16 | N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393
17 | N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393
18 | N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393
19 | N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393
20 | 15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403
21 | 24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403
22 | 48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403
23 | 94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403
24 | 34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403
25 | 48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403
26 | 70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403
27 | 94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403
28 | 122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403
29 | 149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403
30 | 34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403
31 | 48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403
32 | 70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403
33 | 94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403
34 | 122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403
35 | 149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403
36 | 184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403
37 | 243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403
38 | 48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403
39 | 70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403
40 | 94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403
41 | 122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403
42 | 149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403
43 | 184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403
44 | 243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403
45 | 305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403
46 | 490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403
47 | 679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403
48 | 490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403
49 | 679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403
50 | 490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403
51 | 679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403
52 | NFA2X 4x70 | 12.8 | 0.443 | 0.07 | 0.205 | ol

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | int32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | sgen | name | object
16 | sgen | bus | int32
17 | sgen | p_mw | float64
18 | sgen | q_mvar | float64
19 | sgen | sn_mva | float64
20 | sgen | scaling | float64
21 | sgen | in_service | bool
22 | sgen | type | object
23 | sgen | current_source | bool
24 | sgen | controllable | bool
25 | ext_grid | name | object
26 | ext_grid | bus | int32
27 | ext_grid | vm_pu | float64
28 | ext_grid | va_degree | float64
29 | ext_grid | slack_weight | float64
30 | ext_grid | in_service | bool
31 | line | name | object
32 | line | std_type | object
33 | line | from_bus | int32
34 | line | to_bus | int32
35 | line | length_km | float64
36 | line | r_ohm_per_km | float64
37 | line | x_ohm_per_km | float64
38 | line | c_nf_per_km | float64
39 | line | g_us_per_km | float64
40 | line | max_i_ka | float64
41 | line | df | float64
42 | line | parallel | uint32
43 | line | type | object
44 | line | in_service | bool