## Sheet1
|  | Model | Single Level
WEIGHT_OP_LIMITS | 0.001 | Objective | 6989 | kEUR
WINTER | TRUE | Time periods | 48
ELECTRIC_VEHICLES | FALSE | Energy consumed | 16440 | MWh/year
HEAT_PUMPS | FALSE | Nb lines built | 21 | -
MAX_PV_CAPACITY_PER_NODE | 0.4 | Nb substations | 1 | -
PV_SCALE_SUMMER_WINTER | 0.1 | DSO total | 1178 | kEUR
IMP_ELECTRICITY_ENRG_COST | 0.3 | DSO yearly | 428.9 | kEUR/year
IMP_ELECTRICITY_DSO_COST | 0.1 | User | 5825 | kEUR/year
EXP_ELECTRICITY_ENRG_COST | 0.1 | PV | 239.6 | kEUR/year
GRID_CONNECTION_COST | 80 | Grid connection | 1960 | kEUR/year
|  | Energy imported | 3677 | kEUR/year
|  | Energy exported | 51.6 | kEUR/year
|  | PV penetration | 8.4 | MVA
|  | PV production | 558.9 | MWh/MVA/year
|  | PV potential | 1545 | MWh/MVA/year
|  | Energy bought from grid | 12260 | MWh/year
|  | Energy sold to grid | 516 | MWh/year
|  | Substation capacity | 10 | MVA
|  | self sufficiency | 0.4271 | average, [-]
|  | self consumption | 0.7226 | average, [-]
|  | loss | 17.11 | MWh/year
|  | LCOE pv | 0.05103 | kEUR/MWh
|  | LCOE grid | 0.4757 | kEUR/MWh

## Sheet2
|  | Model | Single Level
WEIGHT_OP_LIMITS | 0.01 | Objective | 6988 | kEUR
WINTER | TRUE | Time periods | 48
ELECTRIC_VEHICLES | FALSE | Energy consumed | 16440 | MWh/year
HEAT_PUMPS | FALSE | Nb lines built | 21 | -
MAX_PV_CAPACITY_PER_NODE | 0.4 | Nb substations | 1 | -
PV_SCALE_SUMMER_WINTER | 0.1 | DSO total | 1175 | kEUR
IMP_ELECTRICITY_ENRG_COST | 0.3 | DSO yearly | 428.5 | kEUR/year
IMP_ELECTRICITY_DSO_COST | 0.1 | User | 5825 | kEUR/year
EXP_ELECTRICITY_ENRG_COST | 0.1 | PV | 239.6 | kEUR/year
GRID_CONNECTION_COST | 80 | Grid connection | 1960 | kEUR/year
|  | Energy imported | 3677 | kEUR/year
|  | Energy exported | 51.61 | kEUR/year
|  | PV penetration | 8.4 | MVA
|  | PV production | 559 | MWh/MVA/year
|  | PV potential | 1545 | MWh/MVA/year
|  | Energy bought from grid | 12260 | MWh/year
|  | Energy sold to grid | 516.1 | MWh/year
|  | Substation capacity | 10 | MVA
|  | self sufficiency | 0.4271 | average, [-]
|  | self consumption | 0.7226 | average, [-]
|  | loss | 14.33 | MWh/year
|  | LCOE pv | 0.05103 | kEUR/MWh
|  | LCOE grid | 0.4757 | kEUR/MWh

## Sheet3
|  | Model | Single Level
WEIGHT_OP_LIMITS | 0.1 | Objective | 6988 | kEUR
WINTER | TRUE | Time periods | 48
ELECTRIC_VEHICLES | FALSE | Energy consumed | 16440 | MWh/year
HEAT_PUMPS | FALSE | Nb lines built | 21 | -
MAX_PV_CAPACITY_PER_NODE | 0.4 | Nb substations | 1 | -
PV_SCALE_SUMMER_WINTER | 0.1 | DSO total | 1175 | kEUR
IMP_ELECTRICITY_ENRG_COST | 0.3 | DSO yearly | 428.6 | kEUR/year
IMP_ELECTRICITY_DSO_COST | 0.1 | User | 5825 | kEUR/year
EXP_ELECTRICITY_ENRG_COST | 0.1 | PV | 239.6 | kEUR/year
GRID_CONNECTION_COST | 80 | Grid connection | 1960 | kEUR/year
|  | Energy imported | 3677 | kEUR/year
|  | Energy exported | 52.07 | kEUR/year
|  | PV penetration | 8.4 | MVA
|  | PV production | 559.5 | MWh/MVA/year
|  | PV potential | 1545 | MWh/MVA/year
|  | Energy bought from grid | 12260 | MWh/year
|  | Energy sold to grid | 520.7 | MWh/year
|  | Substation capacity | 10 | MVA
|  | self sufficiency | 0.4271 | average, [-]
|  | self consumption | 0.7226 | average, [-]
|  | loss | 14.58 | MWh/year
|  | LCOE pv | 0.05098 | kEUR/MWh
|  | LCOE grid | 0.4759 | kEUR/MWh

## Sheet4
|  | Model | Single Level
WEIGHT_OP_LIMITS | 0.001 | Objective | 14430 | kEUR
WINTER | TRUE | Time periods | 48
ELECTRIC_VEHICLES | TRUE | Energy consumed | 33200 | MWh/year
HEAT_PUMPS | FALSE | Nb lines built | 21 | -
MAX_PV_CAPACITY_PER_NODE | 0.4 | Nb substations | 1 | -
PV_SCALE_SUMMER_WINTER | 0.1 | DSO total | 1151 | kEUR
IMP_ELECTRICITY_ENRG_COST | 0.3 | DSO yearly | 433.1 | kEUR/year
IMP_ELECTRICITY_DSO_COST | 0.1 | User | 13200 | kEUR/year
EXP_ELECTRICITY_ENRG_COST | 0.1 | PV | 252.7 | kEUR/year
GRID_CONNECTION_COST | 80 | Grid connection | 4484 | kEUR/year
|  | Energy imported | 8558 | kEUR/year
|  | Energy exported | 93.16 | kEUR/year
|  | PV penetration | 8.4 | MVA
|  | PV production | 667 | MWh/MVA/year
|  | PV potential | 1545 | MWh/MVA/year
|  | Energy bought from grid | 28530 | MWh/year
|  | Energy sold to grid | 931.6 | MWh/year
|  | Substation capacity | 10 | MVA
|  | self sufficiency | 0.4037 | average, [-]
|  | self consumption | 0.7398 | average, [-]
|  | loss | 33.03 | MWh/year
|  | LCOE pv | 0.0451 | kEUR/MWh
|  | LCOE grid | 0.4693 | kEUR/MWh

## Sheet5
failure
WEIGHT_OP_LIMITS | 0.001
WINTER | TRUE
ELECTRIC_VEHICLES | FALSE
HEAT_PUMPS | TRUE
MAX_PV_CAPACITY_PER_NODE | 0.4
PV_SCALE_SUMMER_WINTER | 0.1
IMP_ELECTRICITY_ENRG_COST | 0.3
IMP_ELECTRICITY_DSO_COST | 0.1
EXP_ELECTRICITY_ENRG_COST | 0.1
GRID_CONNECTION_COST | 80

## Sheet6
failure
WEIGHT_OP_LIMITS | 0.001
WINTER | TRUE
ELECTRIC_VEHICLES | TRUE
HEAT_PUMPS | TRUE
MAX_PV_CAPACITY_PER_NODE | 0.4
PV_SCALE_SUMMER_WINTER | 0.1
IMP_ELECTRICITY_ENRG_COST | 0.3
IMP_ELECTRICITY_DSO_COST | 0.1
EXP_ELECTRICITY_ENRG_COST | 0.1
GRID_CONNECTION_COST | 80

## Sheet7
|  | Model | Single Level
WEIGHT_OP_LIMITS | 0.001 | Objective | 8439 | kEUR
WINTER | TRUE | Time periods | 48
ELECTRIC_VEHICLES | FALSE | Energy consumed | 16440 | MWh/year
HEAT_PUMPS | FALSE | Nb lines built | 21 | -
MAX_PV_CAPACITY_PER_NODE | 0 | Nb substations | 1 | -
PV_SCALE_SUMMER_WINTER | 0.1 | DSO total | 1175 | kEUR
IMP_ELECTRICITY_ENRG_COST | 0.3 | DSO yearly | 427.3 | kEUR/year
IMP_ELECTRICITY_DSO_COST | 0.1 | User | 7280 | kEUR/year
EXP_ELECTRICITY_ENRG_COST | 0.1 | PV | 0 | kEUR/year
GRID_CONNECTION_COST | 80 | Grid connection | 2349 | kEUR/year
|  | Energy imported | 4931 | kEUR/year
|  | Energy exported | 0 | kEUR/year
|  | PV penetration | 0 | MVA
|  | PV production | NaN | MWh/MVA/year
|  | PV potential | NaN | MWh/MVA/year
|  | Energy bought from grid | 16440 | MWh/year
|  | Energy sold to grid | 0 | MWh/year
|  | Substation capacity | 10 | MVA
|  | self sufficiency | 0 | average, [-]
|  | self consumption | NaN | average, [-]
|  | loss | 18.52 | MWh/year
|  | LCOE pv | NaN | kEUR/MWh
|  | LCOE grid | 0.4429 | kEUR/MWh

## Sheet8
|  | Model | Single Level
WEIGHT_OP_LIMITS | 0.001 | Objective | 6713 | kEUR
WINTER | TRUE | Time periods | 48
ELECTRIC_VEHICLES | FALSE | Energy consumed | 16440 | MWh/year
HEAT_PUMPS | FALSE | Nb lines built | 21 | -
MAX_PV_CAPACITY_PER_NODE | 0.8 | Nb substations | 1 | -
PV_SCALE_SUMMER_WINTER | 0.1 | DSO total | 1200 | kEUR
IMP_ELECTRICITY_ENRG_COST | 0.3 | DSO yearly | 437.8 | kEUR/year
IMP_ELECTRICITY_DSO_COST | 0.1 | User | 5525 | kEUR/year
EXP_ELECTRICITY_ENRG_COST | 0.1 | PV | 404.6 | kEUR/year
GRID_CONNECTION_COST | 80 | Grid connection | 1873 | kEUR/year
|  | Energy imported | 3331 | kEUR/year
|  | Energy exported | 83.28 | kEUR/year
|  | PV penetration | 15.93 | MVA
|  | PV production | 387.2 | MWh/MVA/year
|  | PV potential | 1545 | MWh/MVA/year
|  | Energy bought from grid | 11100 | MWh/year
|  | Energy sold to grid | 832.8 | MWh/year
|  | Substation capacity | 10 | MVA
|  | self sufficiency | 0.4935 | average, [-]
|  | self consumption | 0.6288 | average, [-]
|  | loss | 13.58 | MWh/year
|  | LCOE pv | 0.06562 | kEUR/MWh
|  | LCOE grid | 0.4986 | kEUR/MWh

## Sheet9
|  | Model | Single Level
WEIGHT_OP_LIMITS | 0.001 | Objective | 6510 | kEUR
WINTER | TRUE | Time periods | 48
ELECTRIC_VEHICLES | FALSE | Energy consumed | 16440 | MWh/year
HEAT_PUMPS | FALSE | Nb lines built | 21 | -
MAX_PV_CAPACITY_PER_NODE | 1.6 | Nb substations | 1 | -
PV_SCALE_SUMMER_WINTER | 0.1 | DSO total | 1188 | kEUR
IMP_ELECTRICITY_ENRG_COST | 0.3 | DSO yearly | 432.3 | kEUR/year
IMP_ELECTRICITY_DSO_COST | 0.1 | User | 5337 | kEUR/year
EXP_ELECTRICITY_ENRG_COST | 0.1 | PV | 660.7 | kEUR/year
GRID_CONNECTION_COST | 80 | Grid connection | 1783 | kEUR/year
|  | Energy imported | 3001 | kEUR/year
|  | Energy exported | 108 | kEUR/year
|  | PV penetration | 28.13 | MVA
|  | PV production | 267 | MWh/MVA/year
|  | PV potential | 1545 | MWh/MVA/year
|  | Energy bought from grid | 10000 | MWh/year
|  | Energy sold to grid | 1080 | MWh/year
|  | Substation capacity | 10 | MVA
|  | self sufficiency | 0.539 | average, [-]
|  | self consumption | 0.549 | average, [-]
|  | loss | 17.23 | MWh/year
|  | LCOE pv | 0.08797 | kEUR/MWh
|  | LCOE grid | 0.524 | kEUR/MWh

## Sheet10
|  | Model | Single Level
WEIGHT_OP_LIMITS | 0.001 | Objective | 10750 | kEUR
WINTER | TRUE | Time periods | 48
ELECTRIC_VEHICLES | FALSE | Energy consumed | 16440 | MWh/year
HEAT_PUMPS | FALSE | Nb lines built | 21 | -
MAX_PV_CAPACITY_PER_NODE | 0.4 | Nb substations | 1 | -
PV_SCALE_SUMMER_WINTER | 0.1 | DSO total | 1188 | kEUR
IMP_ELECTRICITY_ENRG_COST | 0.6 | DSO yearly | 447.9 | kEUR/year
IMP_ELECTRICITY_DSO_COST | 0.1 | User | 9502 | kEUR/year
EXP_ELECTRICITY_ENRG_COST | 0.1 | PV | 239.6 | kEUR/year
GRID_CONNECTION_COST | 80 | Grid connection | 1960 | kEUR/year
|  | Energy imported | 7354 | kEUR/year
|  | Energy exported | 51.89 | kEUR/year
|  | PV penetration | 8.4 | MVA
|  | PV production | 559.3 | MWh/MVA/year
|  | PV potential | 1545 | MWh/MVA/year
|  | Energy bought from grid | 12260 | MWh/year
|  | Energy sold to grid | 518.9 | MWh/year
|  | Substation capacity | 10 | MVA
|  | self sufficiency | 0.4271 | average, [-]
|  | self consumption | 0.7226 | average, [-]
|  | loss | 10.43 | MWh/year
|  | LCOE pv | 0.051 | kEUR/MWh
|  | LCOE grid | 0.7891 | kEUR/MWh

## Sheet11
|  | Model | Single Level
WEIGHT_OP_LIMITS | 0.001 | Objective | 14340 | kEUR
WINTER | TRUE | Time periods | 48
ELECTRIC_VEHICLES | FALSE | Energy consumed | 16440 | MWh/year
HEAT_PUMPS | FALSE | Nb lines built | 21 | -
MAX_PV_CAPACITY_PER_NODE | 0.4 | Nb substations | 1 | -
PV_SCALE_SUMMER_WINTER | 0.1 | DSO total | 1165 | kEUR
IMP_ELECTRICITY_ENRG_COST | 0.9 | DSO yearly | 425.9 | kEUR/year
IMP_ELECTRICITY_DSO_COST | 0.1 | User | 13180 | kEUR/year
EXP_ELECTRICITY_ENRG_COST | 0.1 | PV | 239.6 | kEUR/year
GRID_CONNECTION_COST | 80 | Grid connection | 1960 | kEUR/year
|  | Energy imported | 11030 | kEUR/year
|  | Energy exported | 52.37 | kEUR/year
|  | PV penetration | 8.4 | MVA
|  | PV production | 559.9 | MWh/MVA/year
|  | PV potential | 1545 | MWh/MVA/year
|  | Energy bought from grid | 12260 | MWh/year
|  | Energy sold to grid | 523.7 | MWh/year
|  | Substation capacity | 10 | MVA
|  | self sufficiency | 0.4271 | average, [-]
|  | self consumption | 0.7226 | average, [-]
|  | loss | 13.7 | MWh/year
|  | LCOE pv | 0.05095 | kEUR/MWh
|  | LCOE grid | 1.103 | kEUR/MWh

## Sheet12
|  | Model | Single Level
WEIGHT_OP_LIMITS | 0.001 | Objective | 8206 | kEUR
WINTER | TRUE | Time periods | 48
ELECTRIC_VEHICLES | FALSE | Energy consumed | 16440 | MWh/year
HEAT_PUMPS | FALSE | Nb lines built | 21 | -
MAX_PV_CAPACITY_PER_NODE | 0.4 | Nb substations | 1 | -
PV_SCALE_SUMMER_WINTER | 0.1 | DSO total | 1173 | kEUR
IMP_ELECTRICITY_ENRG_COST | 0.3 | DSO yearly | 426.1 | kEUR/year
IMP_ELECTRICITY_DSO_COST | 0.2 | User | 7051 | kEUR/year
EXP_ELECTRICITY_ENRG_COST | 0.1 | PV | 239.6 | kEUR/year
GRID_CONNECTION_COST | 80 | Grid connection | 3134 | kEUR/year
|  | Energy imported | 3677 | kEUR/year
|  | Energy exported | 5.371e-07 | kEUR/year
|  | PV penetration | 8.4 | MVA
|  | PV production | 497.5 | MWh/MVA/year
|  | PV potential | 1545 | MWh/MVA/year
|  | Energy bought from grid | 12260 | MWh/year
|  | Energy sold to grid | 5.371e-06 | MWh/year
|  | Substation capacity | 10 | MVA
|  | self sufficiency | 0.4271 | average, [-]
|  | self consumption | 0.7226 | average, [-]
|  | loss | 20.1 | MWh/year
|  | LCOE pv | 0.05733 | kEUR/MWh
|  | LCOE grid | 0.5557 | kEUR/MWh

## Sheet13
|  | Model | Single Level
WEIGHT_OP_LIMITS | 0.001 | Objective | 9452 | kEUR
WINTER | TRUE | Time periods | 48
ELECTRIC_VEHICLES | FALSE | Energy consumed | 16440 | MWh/year
HEAT_PUMPS | FALSE | Nb lines built | 21 | -
MAX_PV_CAPACITY_PER_NODE | 0.4 | Nb substations | 1 | -
PV_SCALE_SUMMER_WINTER | 0.1 | DSO total | 1146 | kEUR
IMP_ELECTRICITY_ENRG_COST | 0.3 | DSO yearly | 425.9 | kEUR/year
IMP_ELECTRICITY_DSO_COST | 0.3 | User | 8276 | kEUR/year
EXP_ELECTRICITY_ENRG_COST | 0.1 | PV | 239.6 | kEUR/year
GRID_CONNECTION_COST | 80 | Grid connection | 4359 | kEUR/year
|  | Energy imported | 3677 | kEUR/year
|  | Energy exported | 1.045e-05 | kEUR/year
|  | PV penetration | 8.4 | MVA
|  | PV production | 497.5 | MWh/MVA/year
|  | PV potential | 1545 | MWh/MVA/year
|  | Energy bought from grid | 12260 | MWh/year
|  | Energy sold to grid | 0.0001045 | MWh/year
|  | Substation capacity | 10 | MVA
|  | self sufficiency | 0.4271 | average, [-]
|  | self consumption | 0.7226 | average, [-]
|  | loss | 12.56 | MWh/year
|  | LCOE pv | 0.05733 | kEUR/MWh
|  | LCOE grid | 0.6557 | kEUR/MWh

## Sheet14
|  | Model | Single Level
WEIGHT_OP_LIMITS | 0.001 | Objective | 6244 | kEUR
WINTER | TRUE | Time periods | 48
ELECTRIC_VEHICLES | FALSE | Energy consumed | 16440 | MWh/year
HEAT_PUMPS | FALSE | Nb lines built | 21 | -
MAX_PV_CAPACITY_PER_NODE | 0.4 | Nb substations | 1 | -
PV_SCALE_SUMMER_WINTER | 0.1 | DSO total | 1189 | kEUR
IMP_ELECTRICITY_ENRG_COST | 0.3 | DSO yearly | 427.8 | kEUR/year
IMP_ELECTRICITY_DSO_COST | 0.1 | User | 5084 | kEUR/year
EXP_ELECTRICITY_ENRG_COST | 0.2 | PV | 306.8 | kEUR/year
GRID_CONNECTION_COST | 80 | Grid connection | 2744 | kEUR/year
|  | Energy imported | 3677 | kEUR/year
|  | Energy exported | 1644 | kEUR/year
|  | PV penetration | 8.4 | MVA
|  | PV production | 1476 | MWh/MVA/year
|  | PV potential | 1545 | MWh/MVA/year
|  | Energy bought from grid | 12260 | MWh/year
|  | Energy sold to grid | 8221 | MWh/year
|  | Substation capacity | 10 | MVA
|  | self sufficiency | 0.4271 | average, [-]
|  | self consumption | 0.7226 | average, [-]
|  | loss | 33.28 | MWh/year
|  | LCOE pv | 0.02474 | kEUR/MWh
|  | LCOE grid | 1.184 | kEUR/MWh

## Sheet15
|  | Model | Single Level
WEIGHT_OP_LIMITS | 0.001 | Objective | 5385 | kEUR
WINTER | TRUE | Time periods | 48
ELECTRIC_VEHICLES | FALSE | Energy consumed | 16440 | MWh/year
HEAT_PUMPS | FALSE | Nb lines built | 21 | -
MAX_PV_CAPACITY_PER_NODE | 0.4 | Nb substations | 1 | -
PV_SCALE_SUMMER_WINTER | 0.1 | DSO total | 1194 | kEUR
IMP_ELECTRICITY_ENRG_COST | 0.3 | DSO yearly | 428 | kEUR/year
IMP_ELECTRICITY_DSO_COST | 0.1 | User | 4224 | kEUR/year
EXP_ELECTRICITY_ENRG_COST | 0.3 | PV | 330.5 | kEUR/year
GRID_CONNECTION_COST | 80 | Grid connection | 2831 | kEUR/year
|  | Energy imported | 3677 | kEUR/year
|  | Energy exported | 2615 | kEUR/year
|  | PV penetration | 8.4 | MVA
|  | PV production | 1535 | MWh/MVA/year
|  | PV potential | 1545 | MWh/MVA/year
|  | Energy bought from grid | 12260 | MWh/year
|  | Energy sold to grid | 8716 | MWh/year
|  | Substation capacity | 10 | MVA
|  | self sufficiency | 0.4271 | average, [-]
|  | self consumption | 0.7226 | average, [-]
|  | loss | 38.48 | MWh/year
|  | LCOE pv | 0.02563 | kEUR/MWh
|  | LCOE grid | 1.1 | kEUR/MWh

## Sheet16
|  | Model | Single Level
WEIGHT_OP_LIMITS | 0.001 | Objective | 7326 | kEUR
WINTER | TRUE | Time periods | 48
ELECTRIC_VEHICLES | FALSE | Energy consumed | 16440 | MWh/year
HEAT_PUMPS | FALSE | Nb lines built | 21 | -
MAX_PV_CAPACITY_PER_NODE | 0.4 | Nb substations | 1 | -
PV_SCALE_SUMMER_WINTER | 0.1 | DSO total | 1174 | kEUR
IMP_ELECTRICITY_ENRG_COST | 0.3 | DSO yearly | 427.5 | kEUR/year
IMP_ELECTRICITY_DSO_COST | 0.1 | User | 6166 | kEUR/year
EXP_ELECTRICITY_ENRG_COST | 0.1 | PV | 239.6 | kEUR/year
GRID_CONNECTION_COST | 120 | Grid connection | 2301 | kEUR/year
|  | Energy imported | 3677 | kEUR/year
|  | Energy exported | 51.95 | kEUR/year
|  | PV penetration | 8.4 | MVA
|  | PV production | 559.4 | MWh/MVA/year
|  | PV potential | 1545 | MWh/MVA/year
|  | Energy bought from grid | 12260 | MWh/year
|  | Energy sold to grid | 519.5 | MWh/year
|  | Substation capacity | 10 | MVA
|  | self sufficiency | 0.4271 | average, [-]
|  | self consumption | 0.7226 | average, [-]
|  | loss | 16.52 | MWh/year
|  | LCOE pv | 0.05099 | kEUR/MWh
|  | LCOE grid | 0.5049 | kEUR/MWh

## Sheet17
|  | Model | Single Level
WEIGHT_OP_LIMITS | 0.001 | Objective | 7670 | kEUR
WINTER | TRUE | Time periods | 48
ELECTRIC_VEHICLES | FALSE | Energy consumed | 16440 | MWh/year
HEAT_PUMPS | FALSE | Nb lines built | 21 | -
MAX_PV_CAPACITY_PER_NODE | 0.4 | Nb substations | 1 | -
PV_SCALE_SUMMER_WINTER | 0.1 | DSO total | 1179 | kEUR
IMP_ELECTRICITY_ENRG_COST | 0.3 | DSO yearly | 428.5 | kEUR/year
IMP_ELECTRICITY_DSO_COST | 0.1 | User | 6507 | kEUR/year
EXP_ELECTRICITY_ENRG_COST | 0.1 | PV | 239.6 | kEUR/year
GRID_CONNECTION_COST | 160 | Grid connection | 2642 | kEUR/year
|  | Energy imported | 3677 | kEUR/year
|  | Energy exported | 51.44 | kEUR/year
|  | PV penetration | 8.4 | MVA
|  | PV production | 558.8 | MWh/MVA/year
|  | PV potential | 1545 | MWh/MVA/year
|  | Energy bought from grid | 12260 | MWh/year
|  | Energy sold to grid | 514.4 | MWh/year
|  | Substation capacity | 10 | MVA
|  | self sufficiency | 0.4271 | average, [-]
|  | self consumption | 0.7226 | average, [-]
|  | loss | 19.35 | MWh/year
|  | LCOE pv | 0.05105 | kEUR/MWh
|  | LCOE grid | 0.5337 | kEUR/MWh